## With Range
MATRIKS PERIODE PEMETAAN SUHU DAN KELEMBABAN
No. | Ruangan/Nama Alat | No. Ruangan | AHU ID | Lokasi | Merk/Tipe | No Seri Peralatan | Rentang Persyaratan |  | Periode
[7 empty] | Suhu | Kelembaban
1 | Empty Capsule | 1511012 | 15102B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
2 | Quarantine Packing Material | 1511013 | 15102B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
3 | Reject Raw Material | 1511014 | 15102B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
4 | Reject Packaging Material | 1511015 | 15102B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
5 | Psikotropik & Prekursor | 1511035 | 15102B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
6 | Raw Material Warehouse 2 | 1511038 | 15101A | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
7 | Raw Material Warehouse 1 | 1511039 | 15101B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
8 | Primary Packaging Warehouse I&II | 1511040 | 15102 | Gedung Pharma | - | - | ≤ 25℃ | ≤65% | 2 tahun
9 | Retained Raw Material 2 | 1513007 | 15108 | Gedung Pharma | - | - | ≤ 25℃ | ≤70% | 2 tahun
10 | Retained Raw Material 1 | 1513012 | 15108 | Gedung Pharma | - | - | ≤ 25℃ | ≤65% | 2 tahun
11 | Staging Before Weighing & Staging Liquid Storage | 1513013-1513018 | 15108 | Gedung Pharma | - | - | ≤ 25℃ | ≤70% | 2 tahun
12 | Staging | 1513021 | 15108 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
13 | Psiktropika, Prekursor, & Obat-obat Tertentu | 1513044 | 15104A | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
14 | WIP Bulk 2 | 1513059 | 15104B | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
15 | WIP Bulk 1 | 1513060 | 15106 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
16 | WIP Bulk TB | 1513074 | 15111 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
17 | After Weighing TB | 1513076 | 15111 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
18 | Staging Liquid | 1513119 | 15109 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
19 | Ruang Simpan Hasil Trial | 1513131 | 15109 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
20 | Ruang Penyimpanan Bahan Kemas | 1513144 | 15112 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
21 | Ruang Penyimpanan Produk Siap Kemas Psikotropika, Prekursor & Obat-obat Tertentu | 1513159 | 15113 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
22 | Staging Secondary Packaging | 1513163 | 15113 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
23 | Staging Finished Good & Reject | 1513164 | 15113 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
24 | Ruang Karantina Leaflet | 1514006 | 15114A | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
25 | Bottle Warehouse | 1514008 | 15114A | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
26 | Finished Goods Warehouse | 1514012 | 15114B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
27 | Cold Storage | 1513011 | 15108 | Gedung Pharma | - | - | 2℃-8℃ | Tidak Diklasifikasikan | 2 tahun
28 | Psychotropic & Precursor Finished Good Warehouse | 1514020 | 15114B | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
29 | Primary Packaging Warehouse 2nd Floor | 1525016 | 15M202 | Gedung Pharma | - | - | ≤ 25℃ | ≤65% | 2 tahun
30 | Raw Material Warehouse | 1525017 | 15M202 | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
31 | Ruang Penyimpanan Hasil Trial | 1522032 |  | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
32 | Quarantine Intermediate Tablet Non BL 2 | 1523010 | 15208 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
33 | Quarantine Bulk Tablet Non BL 2 | 1523018 | 15208 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
34 | Staging After Weighing | 1523035 | 15206 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
35 | Staging Primary Packaging | 1523048 | 15206 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
36 | Quarantine Bulk Oral Powder Non BL 2 | 1523049 | 15206 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
37 | Staging Secondary Packaging | 1523061 | 15209 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
38 | Staging Finished Good | 1523065 | 15209 | Gedung Pharma | - | - | ≤ 27℃ | ≤70% | 2 tahun
39 | Secondary Packaging Warehouse 2nd Floor | 1525003 | 15M201 | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
40 | Etiquette and Leaflet Warehouse | 1525003A | 15M201 | Gedung Pharma | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
41 | Retained Sample Finished Goods & Finished Goods Prekursor & Psikotropik | 1524058 | 15M203 | Gedung Pharma | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
42 | Simplicia Warehouse | 1711007 | 17107 | Gedung Herbal | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
43 | Raw Material Herbal & Reject Raw Material Herbal | 1711024 & 1711025 |  | Gedung Herbal | - | - | ≤ 25℃ | ≤ 65% | 2 tahun
44 | Cold Storage | 1714013A | - | Gedung Herbal | - | - | 2 - 8 ℃ | Tidak Diklasifikasikan | 2 tahun
45 | Staging Primary Packaging | 1714007 | 17104 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
46 | Staging & retained Raw Material | 1716013 | 17104 | Gedung Herbal | - | - | ≤ 25℃ | ≤ 65% | 2 tahun
47 | Staging Before Weighing | 1716015 | 17104 | Gedung Herbal | - | - | ≤ 25℃ | ≤ 65% | 2 tahun
48 | Weighing Herbal | 1716018 | 17104 | Gedung Herbal | - | - | ≤ 25℃ | ≤70% | 2 tahun
49 | Staging After Weighing | 1716020 | 17104 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
50 | Staging Primary Packaging | 1716029 | 17104 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
51 | Blowing Bottle | 1716034 | 17105 | Gedung Herbal | - | - | ≤ 27℃ | Tidak Diklasifikasikan | 2 tahun
52 | Staging Finished Goods | 1716046 | 17106 | Gedung Herbal | - | - | ≤ 27℃ | Tidak Diklasifikasikan | 2 tahun
53 | Staging Secondary Packaging | 1716047 | 17106 | Gedung Herbal | - | - | ≤ 27℃ | Tidak Diklasifikasikan | 2 tahun
54 | Packaging Warehouse-1 | 1717010A | 17108 | Gedung Herbal | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
55 | Staging After Weighing | 1722005 | 17204 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
56 | WIP BULK | 1722032 | 17204 | Gedung Herbal | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
57 | Empty Capsule | 1722033 | 17204 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
58 | Staging Semi Finished Goods | 1722039 | 17206 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
59 | Staging Primary Packaging | 1722020 | 17206 | Gedung Herbal | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
60 | Staging Finished Goods | 1722045 | 17207 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
61 | Staging Secondary Packaging | 1722046 | 17207 | Gedung Herbal | - | - | ≤ 30℃ | Tidak Diklasifikasikan | 2 tahun
62 | Secondary Packaging Warehouse | 1724005 | 17M101 | Gedung Herbal | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
63 | Returned Reject Room | 1724011 | - | Gedung Herbal | - | - | ≤ 25℃ | Tidak Diklasifikasikan | 2 tahun
Lampiran ke-2 Kode Dokumen : F-I-EM-05-219-02/00 Tanggal Efektif :
Note on B49: Kimia Farma: tapi ga ada di jadwal yang dibuat teguh, apa karna sekarang ruangannya udah jadi MR, harus dicek no ruangannya berapa

## Without Range (hidden)
Attachment-2
Doc. Number |  | : | F-PEM-xx-xxx-xx/00
Date of Issue |  | :
MAPPING PERIOD MATRIX
No. | Room/ Equipment Name |  |  | Room No. | AHU ID | Location | Brand/ Type | Equipment Serial No. | Requirement Range |  | Period
[9 empty] | Temperature | Relative Humidity
1. | Quarantine Raw Material |  |  | 1511012 | 15102B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
2. | Quarantine Packing Material |  |  | 1511013 | 15102B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
3. | Reject Raw Material |  |  | 1511014 | 15102B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
4. | Reject Packaging Material |  |  | 1511015 | 15102B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
5. | Psikotropik & Prekursor |  |  | 1511035 | 15102B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
6. | Raw Material Warehouse (Ambient Temp. Max 30℃) |  |  | 1511038 | 15101A | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
7. | Raw Material Warehouse (Max 25℃) |  |  | 1511039 | 15101B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
8. | Primary Packaging Warehouse I&II |  |  | 1511040 | 15102 | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
9. | Primary Packaging Plastic Bottle Warehouse (Max 25℃) |  |  | 1511041 | 15102 | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
10. | Cold Storage Weighing |  |  | 1513011 | - | Pharma Building, Elevation +0,000 | Emerson and Güntner | ZX 020E and GSF 040.3D/24-ENW50 | 2 - 8℃ | Not defined | 1 year
11. | Retained Raw Material |  |  | 1513012 | 15108 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Not defined | 1 year
12. | Staging Before Weighing |  |  | 1513013 | 15108 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
13. | Liquid Storage |  |  | 1513018 | 15108 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
14. | Staging After Weighing |  |  | 1513021 | 15108 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
15. | WIP Intermediate Non BL |  |  | 1513044 | 15104A | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
16. | WIP Bulk Non BL |  |  | 1513060 | 15106 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
17. | Empty Capsule |  |  | 1513066 | 1510501 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
18. | Before Weighing TB |  |  | 1513074 | 15111 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
19. | After Weighing TB |  |  | 1513076 | 15111 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
20. | Empty Capsule TB |  |  | 1513088 | 15111 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
21. | WIP TB |  |  | 1513099 | 15111 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
22. | Staging Raw Material Liquid |  |  | 1513119 | 15109 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
23. | Holding Tank-1 |  |  | 1513121 | 15109 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
24. | Holding Tank-2 |  |  | 1513123 | 15109 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
25. | Staging Primary Packaging |  |  | 1513133 | 15112 | Pharma Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
26. | Staging Secondary Packaging |  |  | 1513159 | 15113 | Pharma Building, Elevation +0,000 | - | - | 20 - 28℃ | Not defined | 1 year
27. | Staging Finished Goods |  |  | 1513164 | 15113 | Pharma Building, Elevation +0,000 | - | - | 20 - 28℃ | Not defined | 1 year
28. | Reject Bottle |  |  | 1514006 | 15114A | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
29. | Quarantine Bottle |  |  | 1514007 | 15114A | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
30. | Bottle Warehouse |  |  | 1514008 | 15114A | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
31. | Finished Goods Quarantine Area |  |  | 1514011 | 15114B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
32. | Finished Goods Warehouse |  |  | 1514012 | 15114B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
33. | Finished Goods Reject Area |  |  | 1514012A | 15114B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
34. | Quarantine Psikotropik & Prekursor |  |  | 1514013 | 15114B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
35. | Psikotropik & Prekursor Finished Goods |  |  | 1514014 | 15114B | Pharma Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
36. | Primary Packaging Warehouse |  |  | 1525016 | 15M202 | Pharma Building, Elevation +12,000 | - | - | Max. 30℃ | Not defined | 1 year
37. | Raw Material Warehouse |  |  | 1525017 | 15M202 | Pharma Building, Elevation +12,000 | - | - | Max. 30℃ | Not defined | 1 year
38. | Raw Material Cold Storage |  |  | 1521018 | - | Pharma Building, Elevation +12,000 | Emerson and Güntner | ZX 050E and GSF 040.3F/34-ENW50 | 2℃-8℃ | Not defined | 1 year
39. | Staging After Weighing Tablet Non BL2 |  |  | 1523004 | 15208 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
40. | Quarantine Intermediate Tablet Non BL2 |  |  | 1523010 | 15208 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
41. | Quarantine Bulk Tablet Non BL2 |  |  | 1523018 | 15208 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
42. | Staging Primary Packing Tablet Non BL2 |  |  | 1523027 | 15208 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
43. | Staging After Weighing Oral Powder Non BL 2 |  |  | 1523035 | 15206 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
44. | Staging Bottle |  |  | 1523041 | 15206 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
45. | Staging Primary Packing Oral Powder Non BL 2 |  |  | 1523048 | 15206 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
46. | Quarantine Bulk Oral Powder Non BL2 |  |  | 1523049 | 15206 | Pharma Building Elevation +9,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
47. | Staging Secondary Packaging |  |  | 1523061 | 15209 | Pharma Building Elevation +9,000 | - | - | 20 - 28℃ | Not defined | 1 year
48. | Staging Finished Goods |  |  | 1523065 | 15209 | Pharma Building Elevation +9,000 | - | - | 20 - 28℃ | Not defined | 1 year
49. | Retained Sample Raw Material |  |  | 1524056 | 15M204 | Pharma Building, Elevation +14,250 | - | - | Max. 30℃ | Not defined | 1 year
50. | Retained Sample Finished Goods Prekursor & Psikotropik |  |  | 1524057 | 15M203 | Pharma Building, Elevation +14,250 | - | - | Max. 30℃ | Not defined | 1 year
51. | Retained Sample Finished Goods |  |  | 1524058 | 15M203 | Pharma Building, Elevation +14,250 | - | - | Max. 30℃ | Not defined | 1 year
52. | Secondary Packaging Warehouse 2nd Floor |  |  | 1525003 | 15M201 | Pharma Building, Elevation +12,250 | - | - | Max. 30℃ | Not defined | 1 year
53. | Staging After Coding |  |  | 1525005 | 15M201 | Pharma Building, Elevation +12,250 | - | - | Max. 30℃ | Not defined | 1 year
54. | Sampling & Quarantine Simplicia |  |  | 1711005 | 17107 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
55. | Reject Simplicia |  |  | 1711006 | 17107 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
56. | Simplicia Warehouse |  |  | 1711007 | 17107 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
57. | Staging Clean Simplicia |  |  | 1711024 | 17103 | Herbal Building, Elevation +0,000 | - | - | Max. 28℃ | Not defined | 1 year
58. | WIP Extract |  |  | 1714013 | 17102 | Herbal Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
59. | Cold Storage |  |  | 1714013A | - | Herbal Building, Elevation +0,000 | - | - | 2 - 8 ℃ | Not defined | 1 year
60. | Staging & Retained Raw Material |  |  | 1716013 | 17104 | Herbal Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
61. | Staging Before Weighing |  |  | 1716015 | 17104 | Herbal Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
62. | Staging After Weighing-1 |  |  | 1716020 | 17104 | Herbal Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
63. | Staging Primary Packaging |  |  | 1716029 | 17104 | Herbal Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
64. | Staging Bottle |  |  | 1716034 | 17105 | Herbal Building, Elevation +0,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
65. | Staging Finished Goods |  |  | 1716046 | 17106 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
66. | Staging Secondary Packaging |  |  | 1716047 | 17106 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
67. | Finished Goods Warehouse |  |  | 1717010A | 17108 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
68. | Quarantine Finish Goods |  |  | 1717010B | 17108 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
69. | Reject Returned |  |  | 1717010C | 17108 | Herbal Building, Elevation +0,000 | - | - | Max. 30℃ | Not defined | 1 year
70. | Staging Reject Packaging |  |  | 1724002 | 17M201 | Herbal Building, Elevation 6,000 | - | - | Max. 30℃ | Not defined | 1 year
71. | Quarantine Bottle |  |  | 1724003 | 17M101 | Herbal Building, Elevation 6,000 | - | - | Max. 30℃ | Not defined | 1 year
72. | Bottle Warehouse |  |  | 1724004 | 17M101 | Herbal Building, Elevation 6,000 | - | - | Max. 30℃ | Not defined | 1 year
73. | Secondary Packaging Warehouse |  |  | 1724005 | 17M101 | Herbal Building, Elevation 6,000 | - | - | Max. 30℃ | Not defined | 1 year
74. | Quarantine Secondary Packaging |  |  | 1724006 | 17M101 | Herbal Building, Elevation 6,000 | - | - | Max. 30℃ | Not defined | 1 year
75. | Staging After Coding |  |  | 1724008 | 17M101 | Herbal Building, Elevation 6,000 | - | - | Max. 30℃ | Not defined | 1 year
76. | WIP Intermediate |  |  | 1722032 | 17204 | Herbal Building, Elevation +10,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
77. | Empty Capsule |  |  | 1722033 | 17204 | Herbal Building, Elevation +10,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
78. | WIP Bulk |  |  | 1722018 | 17206 | Herbal Building, Elevation +10,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
79. | Staging Primary Packaging |  |  | 1722020 | 17206 | Herbal Building, Elevation +10,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
80. | Staging After Weighing-2 |  |  | 1722005 | 17204 | Herbal Building, Elevation +10,000 | - | - | 20 - 27℃ | Max. 70% | 1 year
81. | Staging Finished Goods |  |  | 1722045 | 17207 | Herbal Building, Elevation +10,000 | - | - | Max. 30℃ | Not defined | 1 year
82. | Staging Secondary Packaging |  |  | 1722046 | 17207 | Herbal Building, Elevation +10,000 | - | - | Max. 30℃ | Not defined | 1 year
83. | Staging After Weighing |  |  | 1912012 | 18101 | Flammable Warehouse | - | - | 20 - 27℃ | Max. 70% | 1 year
84. | Climatic Chamber |  |  | 1524029 | - | Pharma Building, Climatic Chamber Stability Room | Nagano/ ATX 400 | 21817 | 30℃ | 75% | 1 year
85. | Climatic Chamber |  |  | 1524029 | - | Pharma Building, Climatic Chamber Stability Room | Nagano/ ATX 125 | 21816 | 40℃ | 75% | 1 year
86. | Incubator |  |  | 1524044 | - | Pharma Building, Incubator Room | Memmert/ 1PP750 plus | V818.0067 | 30 - 35℃ | Not defined | 1 year
87. | Incubator |  |  | 1524044 | - | Pharma Building, Incubator Room | Memmert/ 188750 plus | V818.00938 | 20 - 25℃ | Not defined | 1 year
88. | Incubator CO2 |  |  | 1524044 | - | Pharma Building, Incubator Room | ESCO/ CCL.050T-8 | 2018-1323303 | Aerob : 32 ± 2.5℃ Anaerob : 43 ± 1℃ | Not defined | 1 year
89. | Oven |  |  | 1524022B | - | Tanur Room | WTB Binder | 990537 | 90 - 110℃ | Not defined | 1 year
90. | Oven |  |  | 1524037 | - | Sterilization Room | WTB Binder/ FED56(E3.1) | 2018 0000012633 |  |  | 1 year
91. | Pharmaceutical Refrigerator |  |  | 1524036 | - | Preparation Room | Panasonic/ MPR-S313 | 16060627 | 2-8℃ | Not defined | 1 year
92. | Pharmaceutical Refrigerator |  |  | 1524021D | - | Reference Standard | Panasonic/ MPR-S313 | 16060636 | 2-8℃ | Not defined | 1 year
93. | Pharmaceutical Refrigerator |  |  | 1524021D | - | Reference Standard | Panasonic/ MPR-S313 | 16060633 | 2-8℃ | Not defined | 1 year
94. | Pharmaceutical Refrigerator |  |  | 1524036 | - | Preparation Room | Sanyo Medicol/ MPR 161 D (H) | 40202714 | 2-8℃ | Not defined | 1 year